## NCR log
NCR No. | Raised on | Raised by | Project / job | Location / area | Reference | Requirement | Non-conformance | Evidence | Severity | Containment | Responsible party | Disposition | Disposition approved by | Root cause | Corrective action | Due | Status | Verified by | Closed on | Linked items | Notes
NCR-031 | 2026-05-12 | P. Lindqvist (site engineer) | Harbour St, Stage 2 | Basement 2, transfer slab pour 3, grid C-D / 4-6 | S-201 rev C note 7; ITP-CON-03 item 4 | Bottom cover 50 mm to reinforcement. | Cover measured 30-35 mm over approx. 4 m2 at C5, where 25 mm bar chairs had been used and two had collapsed. | IMG_5120.jpg; cover meter log CM-0512 | Major | Pour 3 held. Pump rebooked for 14 May. | Northside Steel Fixing | Rework | D. Marsh (structural engineer) | 25 mm chairs delivered and used where 50 mm were specified. Chair size was not checked against the drawing at delivery. | Replace chairs across the bay. Chair size added to the pre-pour check as a hold point. | 2026-05-13 | Closed | D. Marsh (structural engineer) | 2026-05-13 | D-1182 | Pour went ahead 14 May.
NCR-032 | 2026-05-14 | A. Ruiz (QC inspector, line 2) | PO 44817, bracket BR-220 | Line 2, weld cell 3 | Customer drawing BR-220 rev D note 3; WPS-017 rev B | No visible surface porosity on fillet welds. | Surface porosity on 9 of 40 sampled brackets from batch 0514-A. | IMG_7731-7734.jpg; inspection sheet QC-0514 | Major | Batch 0514-A (220 units) quarantined and red-tagged. | Weld cell 3, day shift | Repair | Customer quality engineer (email, 15 May) | Shielding gas flow low after a regulator swap. Gas flow was not on the cell start-up check. | Grind out and re-weld affected brackets. Gas flow reading added to the cell start-up check. | 2026-05-20 | Action in progress |  |  |  | Customer to witness re-inspection of the batch.
NCR-033 | 2026-05-15 | T. Moana (fit-out supervisor) | Level 9 fit-out, 200 Queen St | Level 9, stair 2 lobby, door D9.04 | Door schedule rev F; fire engineering report FER-02 s4.3 | -/60/30 fire door set, tagged, with certification for leaf and frame. | Door delivered and hung with no compliance tag. Supplier cannot yet produce certification for the leaf. | IMG_8802.jpg; delivery docket 55120 | Critical | Door marked not to be signed off. Sign fixed to the frame. | Apex Doors (supplier) | Reject / return |  |  |  | 2026-05-22 | Under review |  |  | D-2047 | Do not accept on a statement. Tag and certificate, or replace the set.

## What each column is for
Column | What it is for
NCR No. | Assigned once, never reused.
Raised on | Date the non-conformance was found.
Raised by | The person who found it, with their role.
Project / job | Project, job, purchase order or product.
Location / area | Where it is: level and gridline, or line and station.
Reference | The document that sets the requirement, with its revision.
Requirement | What the reference says, quoted or measured.
Non-conformance | What was found, measured, and how much of it.
Evidence | Photo filenames, test or inspection record numbers.
Severity | Minor, Major or Critical.
Containment | What was done straight away to stop it spreading.
Responsible party | Who owns the fix.
Disposition | Rework, Repair, Use as is, Reject / return or Scrap.
Disposition approved by | Who accepted the disposition. Required for Repair and Use as is.
Root cause | Why it happened. Not a name.
Corrective action | What changes so it does not happen again.
Due | Date the corrective action is due.
Status | Open, Under review, Disposition approved, Action in progress, Awaiting verification, Closed, Rejected.
Verified by | Someone who is not the responsible party.
Closed on | Date verified and closed.
Linked items | Row numbers of the rework items in your defect or punch list.
Notes | Anything else. Never a substitute for the columns.
From issuesid.com/ncr-template/ - the page explains the columns, three worked NCRs, and where an NCR log breaks.